## Tabelle1
Variable | Variable Name | Read only | Values | Description
06 | I / O port | 1 |  | Read only! WRONG! converting more than one bit to one burns the transformer! Speed is safely defined in variable 29H. Fan speed relays: bit 0 = speed 1 0 = off 1 = on read only bit 1 = speed 2 0 = off 1 = on read only bit 2 = speed 3 0 = off 1 = on read only bit 3 = speed 4 0 = off 1 = on read only bit 4 = speed 5 0 = off 1 = on read only bit 5 = speed 6 0 = off 1 = on read only bit 6 = speed 7 0 = off 1 = on read only bit 7 = speed 8 0 = off 1 = on read only
07 | I / O port | 1 | read only , bit 5 = reheating, 0 = off,1 = on
08 | I / O port | 1 | bit 1 = damper motor position 0 = winter 1 = summer read only bit 2 = fault information relay 0 = open 1 = closed read only bit 3 = input fan 0 = on 1 = off bit 4 = preheating 0 = off 1 = on read only bit 5 = exhaust fan 0 = on 1 = off bit 6 = fireplace / boost switch 0 = open 1 = closed read only
29 | CURRENT FAN SPEED | 1 | Read and Set byte directly Reads or Set FanSpeed from Speed 1 to Speed 8, using the following 8 bits: 01, 03, 07, 0F, 1F, 3F, 7F, FF | Allowed values: 01 = speed 1 03 = speed 2 07 = speed 3 0F = speed 4 1F = speed 5 3F = speed 6 7F = speed FF = speed 8
2A | MAXIMUM MEASURED MOISTURE CONTENT | 1 | read only 33H = 0% RH FFH = 100% RH calculation formula: (x-51) / 2.04
2B | CURRENT MEASURED CO2 CONCENTRATION upper | 1 | read only The CO2 concentration in 16-bit upper byte directly indicates the concentration in PPM
2C | MAXIMUM MEASURED CO2 CONCENTRATION lower | 1 | read only The CO2 concentration in 16-bit subbyte directly indicates the concentration in PPM
2D | CO2 SENSORS INSTALLED ON THE MACHINE | 1 | read only Looks up if up to 5 CO2 sensors are installed. bit 1 = sensor 1, 0 = not installed, 1 = installed ; bit 2 = sensor 2, 0 = not installed, 1 = installed; bit 3 = sensor 3, 0 = not installed, 1 = installed; bit 4 = sensor 4, 0 = not installed, 1 = installed; bit 5 = sensor 5, 0 = not installed, 1 = installed ;
2E | MILLIAMPER / VOLTAGE MESSAGE | 1 | 00H to FFH | read only Current mA / voltage message to the machine on a scale of 00H to FFH
2F | MEASURED% RH CONCENTRATION FROM SENSOR 1 | 1 | 33H = 0% RH FFH = 100% RH | read only calculation formula: (x-51) / 2.04
30 | MEASURED% RH CONCENTRATION FROM SENSOR 2 | 1 | 33H = 0% RH FFH = 100% RH | read only calculation formula: (x-51) / 2.04
32 | OUTDOOR TEMPERATURE | 1 | read only Outdoor temperature on the NTC sensor scale.
33 | InDoorT TEMPERATURE | 1 | read only Exhaust air temperature on the NTC sensor scale.
34 | EXHAUST TEMPERATURE | 1 | read only Exhaust air temperature on the NTC sensor scale.
35 | SUPPLY AIR TEMPERATURE | 1 | read only Supply air temperature on the NTC sensor scale.
36 | FAULT CONDITION ERROR NUMBER | 1 | read only The number of the last fault 05 = Supply air sensor fault 06 = Carbon dioxide alarm 07 = Outdoor sensor fault 08 = Exhaust air sensor fault 09 = Danger of the water coil freezing 0A = Exhaust air sensor fault
55 | POST HEATING ON COUNTER | 1 | Post-heating on time in seconds, counter. as a percentage: X / 2.5
56 | POST HEATING OFF TIME | 1 | Post-heating off-time in seconds, counter. as a percentage: X / 2.5
57 | POST HEATING TARGET VALUE | 1 | read only Target temperature of the air blown into the ventilation zone on the NTC sensor scale.
6D | FLAGS 2 flag variables | 1 | read only bit 0 = CO2 higher speed request 0 = no others. 1 = speed. up bit 1 = CO2 lower speed request 0 = no others. 1 = speed. down bit 2 =% RH lower speed request 0 = no others. 1 = speed. down bit 3 = switch lower speed request 0 = no others. 1 = speed. Down bit 6 = CO2 alarm 0 = no others. 1 = CO2 alarm bit 7 = cell freeze alarm 0 = no others. 1 = risk of freezing
6F | FLAGS 4 flag variables | 1 | read only bit 4 = risk of water coil freezing 0 = no others. 1 = risk of freezing bit 7 = slave / master selection 0 = slave 1 = master
70 | FLAGS 5 flag variables |  | bit 7 = preheating status flag 0 = on 1 = off
71 | FLAGS 6 flag variable | 1 | read only bit 4 = remote control 0 = not working. 1 = function. bit 5 = activating the fireplace switch read the variable and set this to one bit 6 = fireplace / boost function 0 = not working. 1 = function. read only bit 7 = service reminder 0 = off 1 = on read only
79 | FIREPLACE / POWER SWITCH COUNTER | 1 | read only Remaining time of the function in minutes, descending
8F | TRANSMISSION ALLOWED ONLY IN WRITING | 1 | The modules are allowed to send data to the RS-485 bus. DATA = always 0.
91 | TRANSMISSION PROHIBITED |  | write only Modules are prohibited from sending data to the RS-485 bus. DATA = always 0.
A3 | SELECT VARIABLES: INDICATOR LIGHTS | data value has 8 different parameters, each defined by either 0 or 1 at ist bit position | bit 0 = Power key 0 = off 1 = on bit 1 = CO2 key 0 = off 1 = on bit 2 =% RH key 0 = off 1 = on bit 3 = Post Heating key 0 = off 1 = on bit 4 = Filter guard LED 0 = 0ff 1 = on read only bit 5 = Post Heating LED 0 = off 1 = on read only bit 6 = fault LED 0 = off 1 = on read only bit 7 = service reminder 0 = off 1 = on read only
A4 | POST HEATING SETPOINT | 1 | Post-heating target value on the NTC sensor scale.
A5 | MAX FAN SPEED |  | Maximum fan speed that can be set during adjustments. Allowed values: 01 = speed 1 03 = speed 2 07 = speed 3 0F = speed 4 1F = speed 5 3F = speed 6 7F = speed FF = speed 8
A6 | SERVICE REMINDER INTERVAL |  | Service reminder interval in months.
A7 | PREHEATING SWITCHING TEMPERATURE |  | Preheating switching temperature on the NTC sensor scale.
A8 | SUPPLY AIR FAN STOP TEMPERATURE |  | Supply air fan stop temperature on the NTC sensor scale.
A9 | BASIC FAN SPEED |  | Allowed values: 01 = speed 1 03 = speed 2 07 = speed 3 0F = speed 4 1F = speed 5 3F = speed 6 7F = speed FF = speed 8
AA | PROGRAM VARIABLE |  |  | bits 0-3 adjustment interval in 4-bit bit 4 = automatic humidity level search 0 = off 1 = on bit 5 = boost / fireplace switch status 0 = fireplace. 1 = boost switch bit 6 = water / radiator model 0 = electricity 1 = water bit 7 = cascade control 0 = off 1 = on
AB | SERVICE REMINDER MONTHLY COUNTER |  |  | The monthly counter of the service reminder indicates the time remaining in months for the next service alarm. Downward.
AE | BASIC HUMIDITY LEVEL | 1 | 33H = 0% RH FFH = 100% RH | read only calculation formula: (x-51) / 2.04
AF | BYPASS OPERATING TEMPERATURE |  |  | Bypass operating temperature on the NTC sensor scale.
B0 | DC SUPPLY AIR FAN CONTROL SETPOINT |  |  | DC supply air fan control setpoint as a percentage.
B1 | DC EXHAUST FAN CONTROL SETPOINT |  |  | DCI exhaust fan control setpoint as a percentage.
B2 | CELL ANTI-FREEZE TEMPERATURE HYSTERESIS |  | 03H ≅ 1 ° C | Hysteresis of cell antifreeze temperatures, 03H ≅ 1 ° C.
B3 | CARBON DIOXIDE CONTROL SETPOINT 16 BIT |  |  | Carbon control control setpoint in 16-bit, the upper byte directly indicates the concentration PPM
B4 | CARBON DIOXIDE CONTROL SETPOINT 16 BIT |  |  | Carbon control setpoint in 16-bit, lower byte directly indicates PPM concentration
B5 | VARIABLE PROGRAM2 |  |  | bit 0 = Maximum speed limit 0 = with adjustments 1 = always on The use of variables other than those mentioned above is strictly prohibited!

## Tabelle3
Variable | Variable Name | Binär-Wert | Hex-Wert | Bit Position | Parameter defined at bit position | Values | Description
0x06 | I/O port | 0000 0001 | 0x01 | 0 | Speed 1 | 0, 1 | 0 = Off, 1 = On (Read-only)
0x06 | I/O port | 0000 0010 | 0x02 | 1 | Speed 2 | 0, 1 | 0 = Off, 1 = On (Read-only)
0x06 | I/O port | 0000 0100 | 0x04 | 2 | Speed 3 | 0, 1 | 0 = Off, 1 = On (Read-only)
0x06 | I/O port | 0000 1000 | 0x08 | 3 | Speed 4 | 0, 1 | 0 = Off, 1 = On (Read-only)
0x06 | I/O port | 0001 0000 | 0x10 | 4 | Speed 5 | 0, 1 | 0 = Off, 1 = On (Read-only)
0x06 | I/O port | 0010 0000 | 0x20 | 5 | Speed 6 | 0, 1 | 0 = Off, 1 = On (Read-only)
0x06 | I/O port | 0100 0000 | 0x40 | 6 | Speed 7 | 0, 1 | 0 = Off, 1 = On (Read-only)
0x06 | I/O port | 1000 0000 | 0x80 | 7 | Speed 8 | 0, 1 | 0 = Off, 1 = On (Read-only)
0x07 | I/O port | 0001 0000 | 0x10 | 5 | Reheating | 0, 1 | 0 = Off, 1 = On (Read-only)
8 | I/O port | 0000 0001 | 0x01 | 1 | Damper Motor Position | 0, 1 | 0 = Winter, 1 = Summer (Read-only)
8 | I/O port | 0000 0010 | 0x02 | 2 | Fault Information Relay | 0, 1 | 0 = Open, 1 = Closed (Read-only)
8 | I/O port | 0000 0100 | 0x04 | 3 | Input Fan | 0, 1 | 0 = On, 1 = Off
8 | I/O port | 0000 1000 | 0x08 | 4 | Preheating | 0, 1 | 0 = Off, 1 = On (Read-only)
8 | I/O port | 0001 0000 | 0x10 | 5 | Exhaust Fan | 0, 1 | 0 = On, 1 = Off
8 | I/O port | 0010 0000 | 0x20 | 6 | Fireplace/Boost Switch | 0, 1 | 0 = Open, 1 = Closed (Read-only)
29 | CURRENT FAN SPEED | 0000 0001 | 0x01 |  | Speed 1
29 | CURRENT FAN SPEED | 0000 0011 | 0x03 |  | Speed 2
29 | CURRENT FAN SPEED | 0000 0111 | 0x07 |  | Speed 3
29 | CURRENT FAN SPEED | 0000 1111 | 0x0F |  | Speed 4
29 | CURRENT FAN SPEED | 0001 1111 | 0x1F |  | Speed 5
29 | CURRENT FAN SPEED | 0011 1111 | 0x3F |  | Speed 6
29 | CURRENT FAN SPEED | 0111 1111 | 0x7F |  | Speed 7
29 | CURRENT FAN SPEED | 1111 1111 | 0xFF |  | Speed 8
2A | MAXIMUM CURRENT MEASURED MOISTURE CONTENT |  |  | - | - | - | Read-only 33H = 0% RH, FFH = 100% RH calculation formula: (x-51) / 2.04
2B | CURRENT CURRENT MEASURED CO2 CONCENTRATION upper |  |  | - | - | - | Read-only The CO2 concentration in 16-bit upper byte directly indicates the concentration in PPM
2C | MAXIMUM CURRENT MEASURED CO2 CONCENTRATION lower |  |  | - | - | - | Read-only The CO2 concentration in 16-bit subbyte directly indicates the concentration in PPM
2D | MILLIAMPER/VOLTAGE MESSAGE |  |  | 1 | Sensor 1 | 0, 1 | 0 = Not installed, 1 = Installed
2D | MILLIAMPER/VOLTAGE MESSAGE |  |  | 2 | Sensor 2 | 0, 1 | 0 = Not installed, 1 = Installed
2D | MILLIAMPER/VOLTAGE MESSAGE |  |  | 3 | Sensor 3 | 0, 1 | 0 = Not installed, 1 = Installed
2D | MILLIAMPER/VOLTAGE MESSAGE |  |  | 4 | Sensor 4 | 0, 1 | 0 = Not installed, 1 = Installed
2D | MILLIAMPER/VOLTAGE MESSAGE |  |  | 5 | Sensor 5 | 0, 1 | 0 = Not installed, 1 = Installed
2E | CO2 SENSORS INSTALLED ON THE MACHINEMILLIAMPER/VOLTAGE MESSAGE |  |  | - | - | 00H to FFH | Read-only Current mA/voltage message to the machine on a scale of 00H to FFH
2F | MEASURED% RH CONCENTRATION FROM SENSOR 1 |  |  | - | - | 33H = 0% RH, FFH = 100% RH | Read-only calculation formula: (x-51) / 2.04
30 | MEASURED% RH CONCENTRATION FROM SENSOR 2 |  |  | - | - | 33H = 0% RH, FFH = 100% RH | Read-only calculation formula: (x-51) / 2.04
32 | OUTDOOR TEMPERATURE |  |  | - | - | - | Read-only Outdoor temperature on the NTC sensor scale
33 | EXHAUST TEMPERATURE |  |  | - | - | - | Read-only Exhaust air temperature on the NTC sensor scale
34 | InDOOR TEMPERATURE |  |  | - | - | - | Read-only Exhaust air temperature on the NTC sensor scale
35 | SUPPLY AIR TEMPERATURE |  |  | - | - | - | Read-only Supply air temperature on the NTC sensor scale
36 | FAULT CONDITION ERROR NUMBER |  |  | - | - | 05, 06, 07, 08, 09, 0A | Read-only The number of the last fault: 05 = Supply air sensor fault, 06 = Carbon dioxide alarm, 07 = Outdoor sensor fault, 08 = Exhaust air sensor fault, 09 = Danger of the water coil freezing, 0A = Exhaust air sensor fault
36 | FAULT CONDITION ERROR NUMBER |  |  |  |  | 05, 06, 07, 08, 09, 0A | Read-only The number of the last fault: 05 = Supply air sensor fault, 06 = Carbon dioxide alarm, 07 = Outdoor sensor fault, 08 = Exhaust air sensor fault, 09 = Danger of the water coil freezing, 0A = Exhaust air sensor fault
55 | POST HEATING ON COUNTER | [5 empty] | Post-heating on time in seconds, counter (as a percentage: X / 2.5)
56 | POST HEATING OFF TIME | [5 empty] | Post-heating off-time in seconds, counter (as a percentage: X / 2.5)
57 | POST HEATING TARGET VALUE | [5 empty] | Read-only Target temperature of the air blown into the ventilation zone on the NTC sensor scale
6D | FLAGS 2 flag variables |  |  | 0 | CO2 Higher Speed Request | 0, 1
6D | FLAGS 2 flag variables |  |  | 1 | CO2 Lower Speed Request | 0, 1
6D | FLAGS 2 flag variables |  |  | 2 | % RH Lower Speed Request | 0, 1
6D | FLAGS 2 flag variables |  |  | 3 | Switch Lower Speed Request | 0, 1
6D | FLAGS 2 flag variables |  |  | 6 | CO2 Alarm | 0, 1
6D | FLAGS 2 flag variables |  |  | 7 | Cell Freeze Alarm | 0, 1
6F | FLAGS 4 flag variables |  |  | 4 | Risk of Water Coil Freezing | 0, 1 | 0 = No, 1 = Risk of Freezing
6F | FLAGS 4 flag variables |  |  | 7 | Slave/Master Selection | 0, 1 | 0 = Slave, 1 = Master
70 | FLAGS 5 flag variables |  |  | 7 | Preheating Status Flag | 0, 1 | 0 = On, 1 = Off
71 | FLAGS 6 flag variable |  |  | 4 | Remote Control | 0, 1 | 0 = Not Working, 1 = Functioning
71 | FLAGS 6 flag variable |  |  | 5 | Fireplace Switch Activation | 0, 1 | Read the variable and set this to one
71 | FLAGS 6 flag variable |  |  | 6 | Fireplace/Boost Function | 0, 1 | 0 = Not Working, 1 = Functioning (Read-only)
71 | FLAGS 6 flag variable |  |  | 7 | Service Reminder | 0, 1 | 0 = Off, 1 = On (Read-only)
79 | FIREPLACE/POWER SWITCH COUNTER | [5 empty] | Read-only Remaining time of the function in minutes, descending
8F | TRANSMISSION ALLOWED ONLY IN WRITING | [5 empty] | The modules are allowed to send data to the RS-485 bus. DATA = always 0.
91 | TRANSMISSION PROHIBITED | [5 empty] | Write only Modules are prohibited from sending data to the RS-485 bus. DATA = always
A3 | SELECT VARIABLES: INDICATOR LIGHTS |  |  | A3 | 0 | Power Key | 0, 1
A3 | SELECT VARIABLES: INDICATOR LIGHTS |  |  | A3 | 1 | CO2 Key | 0, 1
A3 | SELECT VARIABLES: INDICATOR LIGHTS |  |  | A3 | 2 | % RH Key | 0, 1
A3 | SELECT VARIABLES: INDICATOR LIGHTS |  |  | A3 | 3 | Post Heating Key | 0, 1
A3 | SELECT VARIABLES: INDICATOR LIGHTS |  |  | A3 | 4 | Filter Guard LED | 0, 1
A3 | SELECT VARIABLES: INDICATOR LIGHTS |  |  | A3 | 5 | Post Heating LED | 0, 1
A3 | SELECT VARIABLES: INDICATOR LIGHTS |  |  | A3 | 6 | Fault LED | 0, 1
A3 | SELECT VARIABLES: INDICATOR LIGHTS |  |  | A3 | 7 | Service Reminder LED | 0, 1
A4 | POST HEATING SETPOINT | [5 empty] | Post-heating target value on the NTC sensor scale.
A5 | MAX FAN SPEED |  |  | - | - | 01, 03, 07, 0F, 1F, 3F, 7F, FF | Maximum fan speed that can be set during adjustments. Allowed values: 01 = speed 1, ..., FF = speed 8
A6 | SERVICE REMINDER INTERVAL |  |  | - | - | - | Service reminder interval in months.
A7 | PREHEATING SWITCHING TEMPERATURE |  |  | - | - | - | Preheating switching temperature on the NTC sensor scale.
A8 | SUPPLY AIR FAN STOP TEMPERATURE | [5 empty] | Supply air fan stop temperature on the NTC sensor scale.
A9 | BASIC FAN SPEED |  |  | - | - | 01, 03, 07, 0F, 1F, 3F, 7F, FF | Allowed values: 01 = speed 1, ..., FF = speed 8
AA | PROGRAM VARIABLE |  |  | 0-3 | Adjustment Interval | 4-bit | Adjustment interval in 4-bit
AA | PROGRAM VARIABLE |  |  | 4 | Automatic Humidity Level Search | 0, 1 | 0 = Off, 1 = On
AA | PROGRAM VARIABLE |  |  | 5 | Boost/Fireplace Switch Status | 0, 1 | 0 = Fireplace, 1 = Boost Switch
AA | PROGRAM VARIABLE |  |  | 6 | Water/Radiator Model | 0, 1 | 0 = Electricity, 1 = Water
AA | PROGRAM VARIABLE |  |  | 7 | Cascade Control | 0, 1 | 0 = Off, 1 = On
AB |  |  |  | - | - | - | The monthly counter of the service reminder indicates the time remaining in months for the next service alarm. Downward.
AE | BASIC HUMIDITY LEVEL |  |  | - | - | 33H = 0% RH, FFH = 100% RH | Read-only calculation formula: (x-51) / 2.04
AF | BYPASS OPERATING TEMPERATURE |  |  | - | - | - | Bypass operating temperature on the NTC sensor scale.
B0 | DC SUPPLY AIR FAN CONTROL SETPOINT |  |  | - | - | - | DC supply air fan control setpoint as a percentage.
B1 | DC EXHAUST FAN CONTROL SETPOINT |  |  | - | - | - | DC exhaust fan control setpoint as a percentage.
B2 | CELL ANTI-FREEZE TEMPERATURE HYSTERESIS |  |  | - | - | 03H ≅ 1 °C | Hysteresis of cell antifreeze temperatures, 03H ≅ 1 °C.
B3 | CARBON DIOXIDE CONTROL SETPOINT 16 BIT | [5 empty] | B3 - - - Carbon dioxide control setpoint in 16-bit, the upper byte directly indicates the concentration PPM.
B4 | CARBON DIOXIDE CONTROL SETPOINT 16 BIT | [5 empty] | Carbon dioxide control setpoint in 16-bit, lower byte directly indicates PPM concentration.
B5 | VARIABLE PROGRAM2 |  | B5 | 0 | Maximum Speed Limit | 0, 1 | 0 = With adjustments, 1 = Always On

## Tabelle2
#NAME?
Variable | Variable Name | Binär-Wert | Hex-Wert | Bit Position | Parameter defined at bit position | Values | Description
0x06 | "I/O port" | 0b00000001 | 0x01 | 0 | "Speed 1" | {0 | 1} | "0 = Off | 1 = On (Read-only)"}
0x06 | "I/O port" | 0b00000010 | 0x02 | 1 | "Speed 2" | {0 | 1} | "0 = Off | 1 = On (Read-only)"}
0x06 | "I/O port" | 0b00000100 | 0x04 | 2 | "Speed 3" | {0 | 1} | "0 = Off | 1 = On (Read-only)"}
0x06 | "I/O port" | 0b00001000 | 0x08 | 3 | "Speed 4" | {0 | 1} | "0 = Off | 1 = On (Read-only)"}
0x06 | "I/O port" | 0b00010000 | 0x10 | 4 | "Speed 5" | {0 | 1} | "0 = Off | 1 = On (Read-only)"}
0x06 | "I/O port" | 0b00100000 | 0x20 | 5 | "Speed 6" | {0 | 1} | "0 = Off | 1 = On (Read-only)"}
0x06 | "I/O port" | 0b01000000 | 0x40 | 6 | "Speed 7" | {0 | 1} | "0 = Off | 1 = On (Read-only)"}
0x06 | "I/O port" | 0b10000000 | 0x80 | 7 | "Speed 8" | {0 | 1} | "0 = Off | 1 = On (Read-only)"}
0x07 | "I/O port Reheating" | 0b00010000 | 0x10 | 5 | "Reheating" | {0 | 1} | "0 = Off | 1 = On (Read-only)"}
0x08 | "I/O port" | 0b00000001 | 0x01 | 1 | "Damper Motor Position" | {0 | 1} | "0 = Winter | 1 = Summer (Read-only)"}
0x08 | "I/O port" | 0b00000010 | 0x02 | 2 | "Fault Information Relay" | {0 | 1} | "0 = Open | 1 = Closed (Read-only)"}
0x08 | "I/O port" | 0b00000100 | 0x04 | 3 | "Input Fan" | {0 | 1} | "0 = On | 1 = Off"}
0x08 | "I/O port" | 0b00001000 | 0x08 | 4 | "Preheating" | {0 | 1} | "0 = Off | 1 = On (Read-only)"}
0x08 | "I/O port" | 0b00010000 | 0x10 | 5 | "Exhaust Fan" | {0 | 1} | "0 = On | 1 = Off"}
0x08 | "I/O port" | 0b00100000 | 0x20 | 6 | "Fireplace/Boost Switch" | {0 | 1} | "0 = Open | 1 = Closed (Read-only)"}
0x29 | "CURRENT FAN SPEED" | 0b00000001 | 0x01 | -1 | "" | {0 | 0} | "Speed 1"}
0x29 | "CURRENT FAN SPEED" | 0b00000011 | 0x03 | -1 | "" | {0 | 0} | "Speed 2"}
0x29 | "CURRENT FAN SPEED" | 0b00000111 | 0x07 | -1 | "" | {0 | 0} | "Speed 3"}
0x29 | "CURRENT FAN SPEED" | 0b00001111 | 0x0F | -1 | "" | {0 | 0} | "Speed 4"}
0x29 | "CURRENT FAN SPEED" | 0b00011111 | 0x1F | -1 | "" | {0 | 0} | "Speed 5"}
0x29 | "CURRENT FAN SPEED" | 0b00111111 | 0x3F | -1 | "" | {0 | 0} | "Speed 6"}
0x29 | "CURRENT FAN SPEED" | 0b01111111 | 0x7F | -1 | "" | {0 | 0} | "Speed 7"}
0x29 | "CURRENT FAN SPEED" | 0b11111111 | 0xFF | -1 | "" | {0 | 0} | "Speed 8"}
0x2A | "MAXIMUM CURRENT MEASURED MOISTURE CONTENT" |  |  | -1 | "" | {0 | 0} | "Read-only 33H = 0% RH | FFH = 100% RH calculation formula: (x-51) / 2.04"}
0x2B | "CURRENT CURRENT MEASURED CO2 CONCENTRATION upper" | 0 | 0 | -1 | "" | {0 | 0} | "Read-only The CO2 concentration in 16-bit upper byte directly indicates the concentration in PPM"}
0x2C | "MAXIMUM CURRENT MEASURED CO2 CONCENTRATION lower" | 0 | 0 | -1 | "" | {0 | 0} | "Read-only The CO2 concentration in 16-bit subbyte directly indicates the concentration in PPM"}
0x2D | "MILLIAMPER/VOLTAGE MESSAGE" | 0 | 0 | 1 | "Sensor 1" | {0 | 1} | "0 = Not installed | 1 = Installed"}
0x2D | "MILLIAMPER/VOLTAGE MESSAGE" | 0 | 0 | 2 | "Sensor 2" | {0 | 1} | "0 = Not installed | 1 = Installed"}
0x2D | "MILLIAMPER/VOLTAGE MESSAGE" | 0 | 0 | 3 | "Sensor 3" | {0 | 1} | "0 = Not installed | 1 = Installed"}
0x2D | "MILLIAMPER/VOLTAGE MESSAGE" | 0 | 0 | 4 | "Sensor 4" | {0 | 1} | "0 = Not installed | 1 = Installed"}
0x2D | "MILLIAMPER/VOLTAGE MESSAGE" | 0 | 0 | 5 | "Sensor 5" | {0 | 1} | "0 = Not installed | 1 = Installed"}
0x2E | "CO2 SENSORS INSTALLED ON THE MACHINE" | 0 | 0 | -1 | "" | {0 | 0} | "Read-only Current mA/voltage message to the machine on a scale of 00H to FFH"}
0x2F | "MEASURED% RH CONCENTRATION FROM SENSOR 1" | 0 | 0 | -1 | "" | {0 | 0} | "Read-only calculation formula: (x-51) / 2.04"}
0x30 | "MEASURED% RH CONCENTRATION FROM SENSOR 2" | 0 | 0 | -1 | "" | {0 | 0} | "Read-only calculation formula: (x-51) / 2.04"}
0x32 | "OUTDOOR TEMPERATURE" | 0 | 0 | -1 | "" | {0 | 0} | "Read-only Outdoor temperature on the NTC sensor scale"}
0x33 | "EXHAUST TEMPERATURE" | 0 | 0 | -1 | "" | {0 | 0} | "Read-only Exhaust air temperature on the NTC sensor scale"}
0x34 | "InDOOR TEMPERATURE" | 0 | 0 | -1 | "" | {0 | 0} | "Read-only Exhaust air temperature on the NTC sensor scale"}
0x35 | "SUPPLY AIR TEMPERATURE" | 0 | 0 | -1 | "" | {0 | 0} | "Read-only Supply air temperature on the NTC sensor scale"}
0x36 | "FAULT CONDITION ERROR NUMBER" | 0 | 0 | -1 | "05 | 6 | 7 | 8 | 9 | 0A" | {0 | 0} | "Read-only The number of the last fault: 05 = Supply air sensor fault | 06 = Carbon dioxide alarm | 07 = Outdoor sensor fault | 08 = Exhaust air sensor fault | 09 = Danger of the water coil freezing | 0A = Exhaust air sensor fault"}
0x55 | "POST HEATING ON COUNTER" | 0 | 0 | -1 | "" | {0 | 0} | "Post-heating on time in seconds | counter (as a percentage: X / 2.5)"}
0x56 | "POST HEATING OFF TIME" | 0 | 0 | -1 | "" | {0 | 0} | "Post-heating off-time in seconds | counter (as a percentage: X / 2.5)"}
0x57 | "POST HEATING TARGET VALUE" | 0 | 0 | -1 | "" | {0 | 0} | "Read-only Target temperature of the air blown into the ventilation zone on the NTC sensor scale"}
0x6D | "FLAGS 2 flag variables" | 0 | 0 | 0 | "CO2 Higher Speed Request" | {0 | 1} | ""}
0x6D | "FLAGS 2 flag variables" | 0 | 0 | 1 | "CO2 Lower Speed Request" | {0 | 1} | ""}
0x6D | "FLAGS 2 flag variables" | 0 | 0 | 2 | "% RH Lower Speed Request" | {0 | 1} | ""}
0x6D | "FLAGS 2 flag variables" | 0 | 0 | 3 | "Switch Lower Speed Request" | {0 | 1} | ""}
0x6D | "FLAGS 2 flag variables" | 0 | 0 | 6 | "CO2 Alarm" | {0 | 1} | ""}
0x6D | "FLAGS 2 flag variables" | 0 | 0 | 7 | "Cell Freeze Alarm" | {0 | 1} | ""}
0x6F | "FLAGS 4 flag variables" | 0 | 0 | 4 | "Risk of Water Coil Freezing" | {0 | 1} | "0 = No | 1 = Risk of Freezing"}
0x6F | "FLAGS 4 flag variables" | 0 | 0 | 7 | "Slave/Master Selection" | {0 | 1} | "0 = Slave | 1 = Master"}
0x70 | "FLAGS 5 flag variables" | 0 | 0 | 7 | "Preheating Status Flag" | {0 | 1} | "0 = On | 1 = Off"}
0x71 | "FLAGS 6 flag variable" | 0 | 0 | 4 | "Remote Control" | {0 | 1} | "0 = Not Working | 1 = Functioning"}
0x71 | "FLAGS 6 flag variable" | 0 | 0 | 5 | "Fireplace Switch Activation" | {0 | 1} | "Read the variable and set this to one"}
0x71 | "FLAGS 6 flag variable" | 0 | 0 | 6 | "Fireplace/Boost Function" | {0 | 1} | "0 = Not Working | 1 = Functioning (Read-only)"}
0x71 | "FLAGS 6 flag variable" | 0 | 0 | 7 | "Service Reminder" | {0 | 1} | "0 = Off | 1 = On (Read-only)"}
0x79 | "FIREPLACE/POWER SWITCH COUNTER" | 0 | 0 | -1 | "" | {0 | 0} | "Read-only Remaining time of the function in minutes | descending"}
0x8F | "TRANSMISSION ALLOWED ONLY IN WRITING" | 0 | 0 | -1 | "" | {0 | 0} | "The modules are allowed to send data to the RS-485 bus. DATA = always 0."}
0x91 | "TRANSMISSION PROHIBITED" | 0 | 0 | -1 | "" | {0 | 0} | "Write only Modules are prohibited from sending data to the RS-485 bus. DATA = always"}
0xA3 | "SELECT VARIABLES: INDICATOR LIGHTS" | 0 | 0 | 0 | "Power Key" | {0 | 1} | ""}
0xA3 | "SELECT VARIABLES: INDICATOR LIGHTS" | 0 | 0 | 1 | "CO2 Key" | {0 | 1} | ""}
0xA3 | "SELECT VARIABLES: INDICATOR LIGHTS" | 0 | 0 | 2 | "% RH Key" | {0 | 1} | ""}
0xA3 | "SELECT VARIABLES: INDICATOR LIGHTS" | 0 | 0 | 3 | "Post Heating Key" | {0 | 1} | ""}
0xA3 | "SELECT VARIABLES: INDICATOR LIGHTS" | 0 | 0 | 4 | "Filter Guard LED" | {0 | 1} | ""}
0xA3 | "SELECT VARIABLES: INDICATOR LIGHTS" | 0 | 0 | 5 | "Post Heating LED" | {0 | 1} | ""}
0xA3 | "SELECT VARIABLES: INDICATOR LIGHTS" | 0 | 0 | 6 | "Fault LED" | {0 | 1} | ""}
0xA3 | "SELECT VARIABLES: INDICATOR LIGHTS" | 0 | 0 | 7 | "Service Reminder LED" | {0 | 1} | ""}
0xA4 | "POST HEATING SETPOINT" | 0 | 0 | -1 | "" | {0 | 0} | "Post-heating target value on the NTC sensor scale."}
0xA5 | "MAX FAN SPEED" | 0 | 0 | -1 | "" | {0 | 0} | "01 | 3 | 7 | 0F | 1F | 3F | 7F | FF Maximum fan speed that can be set during adjustments. Allowed values: 01 = speed 1 | ... | FF = speed 8"}
0xA6 | "SERVICE REMINDER INTERVAL" | 0 | 0 | -1 | "" | {0 | 0} | "Service reminder interval in months."}
0xA7 | "PREHEATING SWITCHING TEMPERATURE" | 0 | 0 | -1 | "" | {0 | 0} | "Preheating switching temperature on the NTC sensor scale."}
0xA8 | "SUPPLY AIR FAN STOP TEMPERATURE" | 0 | 0 | -1 | "" | {0 | 0} | "Supply air fan stop temperature on the NTC sensor scale."}
0xA9 | "BASIC FAN SPEED" | 0 | 0 | -1 | "" | {0 | 0} | "01 | 3 | 7 | 0F | 1F | 3F | 7F | FF Allowed values: 01 = speed 1 | ... | FF = speed 8"}
0xAA | "PROGRAM VARIABLE" | 0 | 0 | 0 | "Adjustment Interval" | {0 | 0} | "4-bit Adjustment interval in 4-bit"}
0xAA | "PROGRAM VARIABLE" | 0 | 0 | 4 | "Automatic Humidity Level Search" | {0 | 1} | "0 = Off | 1 = On"}
0xAA | "PROGRAM VARIABLE" | 0 | 0 | 5 | "Boost/Fireplace Switch Status" | {0 | 1} | "0 = Fireplace | 1 = Boost Switch"}
0xAA | "PROGRAM VARIABLE" | 0 | 0 | 6 | "Water/Radiator Model" | {0 | 1} | "0 = Electricity | 1 = Water"}
0xAA | "PROGRAM VARIABLE" | 0 | 0 | 7 | "Cascade Control" | {0 | 1} | "0 = Off | 1 = On"}
0xAB | "" | 0 | 0 | -1 | "" | {0 | 0} | "The monthly counter of the service reminder indicates the time remaining in months for the next service alarm. Downward."}
0xAE | "BASIC HUMIDITY LEVEL" | 0 | 0 | -1 | "" | {0 | 0} | "33H = 0% RH | FFH = 100% RH Read-only calculation formula: (x-51) / 2.04"}
0xAF | "BYPASS OPERATING TEMPERATURE" | 0 | 0 | -1 | "" | {0 | 0} | "Bypass operating temperature on the NTC sensor scale."}
0xB0 | "DC SUPPLY AIR FAN CONTROL SETPOINT" | 0 | 0 | -1 | "" | {0 | 0} | "DC supply air fan control setpoint as a percentage."}
0xB1 | "DC EXHAUST FAN CONTROL SETPOINT" | 0 | 0 | -1 | "" | {0 | 0} | "DC exhaust fan control setpoint as a percentage."}
0xB2 | "CELL ANTI-FREEZE TEMPERATURE HYSTERESIS" | 0 | 0 | -1 | "" | {0 | 0} | "03H ≅ 1 °C Hysteresis of cell antifreeze temperatures | 03H ≅ 1 °C."}
0xB3 | "CARBON DIOXIDE CONTROL SETPOINT 16 BIT" | 0 | 0 | -1 | "" | {0 | 0} | "B3 - - - Carbon dioxide control setpoint in 16-bit | the upper byte directly indicates the concentration PPM."}
0xB4 | "CARBON DIOXIDE CONTROL SETPOINT 16 BIT" | 0 | 0 | -1 | "" | {0 | 0} | "Carbon dioxide control setpoint in 16-bit | lower byte directly indicates PPM concentration."}
0xB5 | "VARIABLE PROGRAM2" | 0 | 0 | 0 | "Maximum Speed Limit" | {0 | 1} | "0 = With adjustments | 1 = Always On"}